Inspect and document Natural Gas (NG) Distribution Pipe and Service Connections by the following checklist.

| General |  |
| --- | --- |
| Project Name | Engineer of Record |
| Project Number | General Contractor |
| Project Manager | Mechanical Contractor |
| Inspection Requirements |  |
| Records Review Initial Date Natural gas flow modeled and reviewed _________ Preconstruction purge plan submitted and approved _________ Post construction purge and service restoration plan submitted and approved _________ Construction Risk Management Plans reviewed (if applicable) _________ Excavation permits reviewed (if applicable) _________ Welding Certificates meet requirements and on file _________ Operator Certifications meet requirements & on file (F1, F2, E1, E2, etc.) See Appendix A – List of Covered Tasks _________ Submittal provided on the type of PE Fusion Machine to be used _________ Weld Non Destructive Test reports reviewed and on file _________ Pressure test (90 PSIG) and charted for 24 hours complete, passed, & original filed with Utilities _________ Pipe materials Material Test Records on file and meet Specification _________ Directional bore slurry submittal reviewed (if applicable) _________ Outage notifications posted (if applicable) _________ Hot tapping materials and procedures approved (if app.) _________ A/E field reports reviewed & filed _________ A/E Review/Authorization to put in service received _________ Post Start-up Inspection for Building Gas Outages (if applicable) Completed testing to verify building gas system is leak free. Verify and confirm w/ customer, building equipment operator to ensure proper restoration of natural gas service (gas pressure within limits, pilots relit, equipment started up) | Mechanical, Piping Field Inspection OSU Utility marking has been completed before excavation OUPS Utility marking has been completed for Columbia Gas point of service areas and/or campus boundary areas with Public Utilities Purge completed prior to repairs/welding (if applicable) Tracer wire is continuous (no breaks) and installed Inspect welds – visual, UT or radiographic Buried depth of 36” minimum (Class 4 per B31.8) Confirm that survey personnel have located pipe, valves, test connections and anodes Inspect trench bedding and backfill material (sand) Verify pipeline clearance from other utilities meets BDS Pipe sleeves/other protection installed (if applicable) Correct slurry installation for directional bore (if applicable) Inspect pipe Inspect pipe coating (if applicable) Inspect structural supports, bolts, anchors Inspect valves, confirm type, and location Inspect and confirm valve box installation Inspect/verify insulation flanges and risers at transition points from buried to exposed inside tunnels & at buildings Cathodic (Anode) protection sized properly and installed (if applicable) Check for shorts at cathodic test stations & record voltages (if app.) Confirm that all tags, labels are installed Utility non-detectable marking tape is installed Complete start-up purge by bleeding off air or nitrogen Purge and cap completed on demo’d/abandoned piping (if applicable) Inspect meter installation – Coordinate w/ OSU ESS Verify meter configuration programming and communications – Coordinate w/ OSU ESS |
| Comments, Description of Work, Routing of Natural Gas Line |  |
| BDS Div Compliance. yes no, state reason: |  |
| For gas service to new or major renovation buildings, the following is required before gas service valves can be opened: ODIC State Inspection completed Records of building piping pressure tests have been provided to Utilities |  |
| Signatures |  |
| Inspected by Date | Reviewed and Approved (with conditions) by Date |
| Final inspection (if conditionally approved) by Date | Final Review and Approval by Date |
| Energized by Date | cc: Distribution Manager, Shop Supervisor, OSU Utilities Project Representative |